## Slide 1: Analysis of Propane Gas Fire Experiments and Simulations in Residential Scale Structures
Joseph M. Willi
Master of Science Thesis Defense
May 5, 2017

## Slide 2
Introduction
Experimental Setup
Experimental Procedures
FDS Simulation Description
Results and Discussion
Summary
Overview

## Slide 3: Introduction
Nine experiments in two structures
Numerous types of measurements
FDS (version 6.5.3) simulations of each experiment
Significant addition to validation guide
Notes: Experiments apart of larger set of tests; 53 FDS experiments, handful are in residential size structures, none in two-story
-- Picture of smokeview model; burner model
-- Difference between verification validation

## Slide 4: Experimental Setup

## Slide 5: Test Structures
Interlocking concrete block walls
Steel studs set to 16” centers
Two layers of 5/8” Type X gypsum board
Layer of ½” Durock cement board on top of gypsum board
Ceiling covered by two layers of 0.5 in. durock board
Wood truss joist I-beams ceiling

## Slide 6: East Structure
Notes: Highlight 2x2x4 blocks, single story, picture is of the north side

## Slide 7: East Structure
Notes: Entire structure - 24’x40’
Front and back rooms – 20’x12’, middle room 12’x10’
highlight doorways, sealed off room, ceiling height

## Slide 8: West Structure
Notes: -- North side of structure; big differentiating factor between this and east structure is second story
-- notice ground floor similar to single-story structure 2x2x4 blocks, double doors on north side
--

## Slide 9: West Structure – 1st Floor
Notes: English units, designed like basement with walk out doors, stairs
7.25” rise/7.5” run
39’ x 23’ => interior space ~ 35’x 16’

## Slide 10: West Structure – 2nd Floor
Notes: 0.8 m => 32” door
0.9 m => 36” door
Walls wood framed with 2x4s set to 16 in centers, two layers of 5/8” Type X gypsum board with a layer of ½” Durock cement board on top
Outer walls on 2nd floor had 7/16” OSB and 5/16” fiber cement lap siding

## Slide 11: Fire Source
Three propane gas burners
Notes: 2’ x 2’ about 6” above the ground

## Slide 12: Fire Source
Provided by propane supply truck
Notes: Propane supply for commercial industrial applications

## Slide 13: Fire Source
Controlled and measured at rotary gas meter
Notes: Zoom into each part of apparatus

## Slide 14: Fire Source
Uncertainty analysis
Notes: Add picture of meter and truck

## Slide 15: Instrumentation
Thermocouples
Gas species concentrations
Bi-directional Probes
Heat flux gauges
Notes: Floor plans with each type of instrumentation highlighted, uncertainty described

## Slide 16: Experimental Procedures

## Slide 17: Tests 2-4

## Slide 18: Tests 2-4
Notes: ~ 3 minutes between burner ignitions
About 60 seconds til first door
2 minutes until 2nd double door
60 seconds until rear door

## Slide 19: Tests 2-4
Notes: ~ 2 minutes between south door and first burner off
~ 2 minutes between next burners being extinguished
~ PPV after the test to help cool down structure

## Slide 20: Tests 5 & 6
Three “sequences” per test
Use of roof vent and double doors
All burners ignited at once

## Slide 21: Test 5

## Slide 22: Test 5

## Slide 23: Test 6

## Slide 24: Test 6

## Slide 25: Tests 22-25
Three “sequences” per test
Use of roof vent and double doors
All burners ignited at once

## Slide 26: Tests 22 & 23

## Slide 27: Tests 24 & 25

## Slide 28: FDS Simulation Description

## Slide 29: Computational Domain
East Tests: (x, y, z)  (14 m, 8 m, 3 m)
West Tests: (x, y, z)  (14 m, 8 m, 5.4 m)
Eight equally sized meshes
Notes: -- Smokeview pictures; grid
-- Equally sized meshes per simulation to utilize MPI-parallell processing on multi-processor Linux machine

## Slide 30: Mesh Sensitivity Analysis
Coarse (14 cm), medium (10 cm), fine (7 cm or 5 cm)

## Slide 31: Source Fire Characterization
Steel sides, top surface specified mass flux of propane
Single-step reaction mechanism
Notes: -- Reaction mechanisms for combustion in all simulations default mixing controlled, simple chemistry model

## Slide 32: Timing Information
Vents modeled

## Slide 33: Defined Materials
Four materials were defined using MATL namelist group

## Slide 34: Defined Instrumentation
Instrumentation defined using FDS devices

## Slide 35: Results and Discussion

## Slide 36: Summary Plots

## Slide 37: Conclusion