## Slide 1: Analysis of Propane Gas Fire Experiments and Simulations in Residential Scale Structures
Joseph M. Willi
Master of Science Thesis Defense
May 5, 2017

## Slide 2
Background & Motivation
Experimental Setup
Experimental Procedures
FDS Simulation Description
Results and Discussion
Summary
Overview

## Slide 3: Background
Nine experiments in two structures
Propane gas burners used as fire source
Doors and other vents opened and closed to change ventilation
FDS (version 6.5.3) simulations of each experiment
Notes: -- Nine experiments part of larger set of experiments, everything from cold flow tests with ppv fans to nine burner tests, to tests with much larger fuel loads, as pictured here
-- Three gas burners with propane as the fuel used for each fire; controlled by high-precision turn valves, total displaced gas volume measured by rotary gas meter
-- Different doors and vents opened during tests to change ventilation within the compartment
-- While gas temperature, velocity, carbon dioxide/O2 concentrations, and heat flux were measured at different points throughout

## Slide 4: Fire Dynamics Simulator
CFD model of fire-driven fluid flow emphasis on smoke and heat transport from fires
Developed and maintained by NIST
Evaluation of program well-documented by NIST in verification guide[1] and validation guide[2]
Notes: -- CFD model fire-drive flow; solves a form of navier stokes equations for low-speed (Ma < 0.3), thermally driven flows with emphasis on smoke & heat transport from fires
-- Most popular program used by FPEs to predict fire dynamics and smoke movement for potential fire scenarios
-- Evaluation crucial to determine limitations and acceptable uses of FDS

## Slide 5: Verification vs. Validation
Verification checks the math
Validation checks the physics
Compare model results to experimental measurements
52 experiments documented in FDS Validation Guide
Nine burner tests will provide crucial addition to validation database
Notes: -- Verification: numerical model being solved correctly,
-- Validation: checks that the governing equations are appropriate for specific application being modeled
-- 52 FDS experiments, handful are in residential size structures, none in two-story

## Slide 6: Experimental Setup
Notes: -- Pictures of structures?

## Slide 7: East Structure
Notes: Highlight 2x2x4 blocks, single story, picture is of the north side

## Slide 8: East Structure
Notes: Entire structure - 24’x40’
Front and back rooms – 20’x12’, middle room 12’x10’
highlight doorways, sealed off room, ceiling height

## Slide 9: West Structure
Notes: -- North side of structure; big differentiating factor between this and east structure is second story
-- notice ground floor similar to single-story structure 2x2x4 blocks, double doors on north side
--

## Slide 10: West Structure – 1st Floor
Notes: English units, designed like basement with walk out doors, stairs
7.25” rise/7.5” run

## Slide 11: West Structure – 1st Floor
Notes: 39’ x 23’ => interior space ~ 35’x 16’
7.25” rise/7.5” run

## Slide 12: West Structure – 2nd Floor
Notes: 0.8 m => 32” door
0.9 m => 36” door
Walls wood framed with 2x4s set to 16 in centers, two layers of 5/8” Type X gypsum board with a layer of ½” Durock cement board on top
Outer walls on 2nd floor had 7/16” OSB and 5/16” fiber cement lap siding

## Slide 13: Fire Source
Three propane gas burners
Notes: 2’ x 2’ about 6” above the ground

## Slide 14: Fire Source
Provided by propane supply truck
Notes: Propane supply for commercial industrial applications

## Slide 15: Fire Source
Flow controlled and measured at rotary gas meter
Total expanded uncertainty associated with HRR measurement[3] – 8 %
Notes: Zoom into each part of apparatus

## Slide 16: Instrumentation
Thermocouples
Gas sampling
Bi-directional probes (BDPs)
Heat flux gauges
Notes: Floor plans with each type of instrumentation highlighted, uncertainty described

## Slide 17: East Structure Instrumentation
Thermocouple arrays
Notes: 8 per array, 1 “ from ceiling, 12 “ apart after that

## Slide 18: East Structure Instrumentation
Gas sampling locations
Notes: 4 ft above floor

## Slide 19: East Structure Instrumentation
BDP array

## Slide 20: East Structure Instrumentation
Heat flux gauges
Notes: 6” above floor looking at ceiling

## Slide 21: West Structure Instrumentation
Thermocouple arrays – 1st Floor

## Slide 22: West Structure Instrumentation
Gas sampling location – 1st Floor

## Slide 23: West Structure Instrumentation
Thermocouple arrays – 2nd Floor

## Slide 24: West Structure Instrumentation
Gas sampling location – 2nd Floor

## Slide 25: West Structure Instrumentation
BDP array – 2nd Floor

## Slide 26: West Structure Instrumentation
Heat flux gauges – 2nd Floor

## Slide 27: Experimental Procedures

## Slide 28: Overview of Experiments

## Slide 29: Tests 2-4 Heat Release Rate
Estimated via McCaffrey, Quintiere, and Harkleroad (MQH) correlation[9]:
HGL temperatures estimated using thermocouple data
Notes: -- h_k is the effective heat transfer coefficient; calculated by k/thickness
-- A_T is total area of compartment enclosing surfaces

## Slide 30: Tests 2-4
Notes: ~ 3 minutes between burner ignitions
About 60 seconds til first door
2 minutes until 2nd double door
60 seconds until rear door

## Slide 31: Tests 2-4
Notes: ~ 2 minutes between south door and first burner off
~ 2 minutes between next burners being extinguished
~ PPV after the test to help cool down structure

## Slide 32: Overview of Experiments

## Slide 33: Test 5

## Slide 34: Test 5

## Slide 35: Test 6

## Slide 36: Overview of Experiments

## Slide 37: Tests 22 & 23

## Slide 38: Tests 24 & 25

## Slide 39: FDS Simulation Description
Notes: Pictures of smokeview structures

## Slide 40: Computational Domain
Simulation domain divided into 3D rectangular computational cells
Gas density, velocity, temperature, pressure, species concentration calculated within each grid cell
Notes: -- Using laws of mass, momentum, and energy conservation…

## Slide 41: Computational Domain
User specifies grid cell size
Smaller cells  higher resolution
More cells  higher computational cost
How should grid cell size be selected?

## Slide 42: Grid Cell Size Selection
FDS User Guide[10] describes calculating non-dimensional expression / for buoyant plume simulations in which
Suggested that / values from 4 to 16 generate adequate results[11]
Notes: -- cp specific heat of surrounding air
-- delta x nominal grid cell size

## Slide 43: Grid Cell Size Selection
Mesh sensitivity study performed for Test 4 & 25 simulations
Coarse (14 cm), medium (10 cm), and fine (5 cm or 7 cm) grids evaluated
Correspond to / values of:
  5 to 7 for coarse grid
  8 to 11 for medium grid
  15 to 20 for fine grid
/ similar for East and West simulations
Notes: -- Equally sized meshes per simulation to utilize MPI-parallell processing on multi-processor Linux machine

## Slide 44: Mesh Sensitivity Analysis
East Structure – Ceiling Jet Temperature

## Slide 45: Mesh Sensitivity Analysis
East Structure – Oxygen Concentration

## Slide 46: Mesh Sensitivity Analysis
West Structure – Ceiling Jet Temperature

## Slide 47: Mesh Sensitivity Analysis
West Structure – Oxygen Concentration

## Slide 48: Grid Cell Size Selection
Run times:
Medium grid cell size selected (10 cm)
  East Structure: 336,000 computational cells
  West Structure: 604,800 computational cells
Cells divided into eight equally sized meshes
Notes: -- Smokeview pictures; grid
-- Equally sized meshes per simulation to utilize MPI-parallell processing on multi-processor Linux machine

## Slide 49: Source Fire Characterization
Steel sides, top surface specified mass flux of propane based on
Notes: -- Reaction mechanisms for combustion in all simulations default mixing controlled, simple chemistry model
-- Smokeview picture of burners
-- Value of Delta h_c

## Slide 50: Other Defined Parameters
Four materials explicitly defined
Instrumentation defined using FDS devices
Notes: -- Add correct refs to table

## Slide 51: Results and Discussion

## Slide 52: Types of Data Plots
Two types of plots presented for each data quantity
  Experimental and FDS simulation data plots
  Summary log/log scatter plots similar to those presented in FDS Validation Guide
Intended to summarize uncertainty of model in predicting given measurement[14]
Notes: Hot gas layer T, ceiling jet T, individual TCs in TC arrays, CO2 and O2 concentrations, Gas velocity, total heat flux

## Slide 53: Summary Plots
Define , value from model data and , corresponding value measured during experiment
: average value over 30 second period in which
  At least one burner ignited
  Only natural ventilation present in structure
Only data from Tests 5-6 and Tests 22-25 considered
Notes: -- assume ln(M/E) is normally distributed

## Slide 54: Summary Plots
Calculate mean and standard deviation of distribution by first calculating
Assume is normally distributed
(Note: assumption tested and results shown in
FDS Validation Guide)
Notes: -- assume ln(M/E) is normally distributed

## Slide 55: Summary Plots
Standard deviation of the log of a normally distributed random variable standard deviation divided by its mean
Least squares estimate of standard deviation of the combined distribution defined as
Impose following constraint:
Notes: -- assume ln(M/E) is normally distributed
-- know sigma e

## Slide 56: Summary Plots
The following is produced
And using the mean of the distribution, a bias factor can be estimated as
Notes: -- Example from FDS Validation Guide?
-- describe gray points; solid lines expected values, dashed lines +/-, etc.

## Slide 57: HGL Temperature Estimation
Average temperature of smoke-laden upper layer
Using vertical temperature profile from each thermocouple array, HGL temperature and depth can be estimated[15]
Take as floor and as room’s ceiling and
  : upper layer temperature
  : lower layer temperature
  : the HGL interface height
Notes: -- Picture of HGL

## Slide 58
Begin by computing values of and
Use values to calculate
where is temperature from lowest thermocouple and
is the average upper layer temperature defined by
HGL Temperature Estimation

## Slide 59: HGL Data Plot – Test 22

## Slide 60: HGL Summary Plot

## Slide 61: Ceiling Jet Temperature
Temperature near ceiling
Useful to predict alarm, sprinkler, smoke detector activation times
Taken as top thermocouple temperature
Notes: Hot gas layer T, ceiling jet T, individual TCs in TC arrays, CO2 and O2 concentrations, Gas velocity, total heat flux

## Slide 62: Ceiling Jet Data Plot – Test 4

## Slide 63: Ceiling Jet Summary Plot

## Slide 64: TC Array Data Plot – Test 4

## Slide 65: TC Array Summary Plot

## Slide 66: O2 Concentration Data Plot – Test 24

## Slide 67: O2 Concentration Summary Plot

## Slide 68: CO2 Concentration Data Plot – Test 6

## Slide 69: CO2 Concentration Summary Plot

## Slide 70: Gas Velocity Data Plot – Test 6

## Slide 71: Gas Velocity Summary Plot

## Slide 72: Heat Flux Data Plot – Test 3

## Slide 73: Heat Flux Summary Plot

## Slide 74: Summary of Results

## Slide 75: Summary of Results
Agreement between experimental data and FDS model data
HGL, ceiling jet, and heat flux better than expected
Gas species model bias worse than value from FDS Validation Guide; relative model standard deviation 0.01 or 0.02 worse
Gas velocity contains largest discrepancy

## Slide 76: Summary of Results
Discrepancy in gas velocity values could be a result of
  Conducted outdoors
  BDPs had the highest exp uncertainty
  LES CFD models limited when it comes to turbulent gas flow at fine resolutions

## Slide 77: Conclusion
Propane gas burner tests conducted amongst two residential-sized structures
Experiments modeled using FDS
Results compared to measured data
Sufficient agreement with largest discrepancy gas velocity
Results add an important data set to FDS validation guide

## Slide 78: Conclusion
Set of experiments added in most recent version of FDS Validation Guide

## Slide 79: Acknowledgements
NIST and specifically the following individuals
  Dan Madrzykowski
  Kristopher Overholt
  Roy McLane
  Keith Stakes
  Craig Weinschenk
Delaware County Emergency Services Training Center, namely Deputy Director Kerby Kerber
Dr. Kevin McGrattan of NIST
Dr. James Milke
Dr. Arnaud Trouvé & Dr. Craig Weinschenk
Notes: And of course the audience!

## Slide 80: Questions?

## Slide 81: Thermocouples
Bare-bead, type K from OMEGA Engineering Inc.
Eight thermocouples per array, spaced 12” apart with top 1” below ceiling
Total expanded uncertainty[4,5] – 15 %

## Slide 82: Gas Sampling
System from California Analytical Instruments, Inc.
Pulled through 3/8” stainless steel tubing located 4’ above floor and through filter in dry ice to cool sample
Total expanded uncertainty[6] – 12 %

## Slide 83: Bi-Directional Probes
Each probe with Setra 264 pressure transducer and bare-bead, type K thermocouple
East Structure: three probes centered in roof vent
West Structure: eight probes centered in doorway
Total expanded uncertainty[7] – 14 % to 22 % (18 % used for analysis)
Notes: Each probe in doorway centered and spaced 10” apart with top one 3” below soffit

## Slide 84: Total Heat Flux
Water-cooled, Schmidt- Boelter total heat flux gauges
East Structure: single gauge 6” above floor, facing ceiling
West Structure: pair of gauges 3’ 3” above floor, one facing ceiling, one facing wall
Total expanded uncertainty[8] – 8 %

## Slide 85: Propane Properties
kg/m3
kJ/kg
R.C. Reid, J.M. Prausnitz, and B.E. Poling. Properties of Gases and Liquids. McGraw-Hill, New York, 4th edition, 1987.

## Slide 86: FDS Vent Example

## Slide 87: Leakage Measurements
East Structure – 0.024 m2
West Structure
  Stairway door closed – 0.027 m2
  Stairway door opened – 0.054 m2
  Stairway in ”closed” position – 0.048 m2

## Slide 88: Source Fire Combustion
Two-step, fast reaction mechanism with gas phase suppression set to FALSE
Best way to handle set of reactions, extinction model for multiple fast reactions not very robust
Notes: -- Reaction mechanisms for combustion in all simulations default mixing controlled, simple chemistry model
-- Smokeview picture of burners
-- Value of Delta h_c

## Slide 89: References
[1] K. McGrattan, S. Hostikka, R. McDermott, J. Floyd, C. Weinschenk, and K.
Overholt. Fire Dynamics Simulator, Technical Reference Guide, Volume 2:
Verification. National Institute of Standards and Technology, Gaithersburg,
Maryland, USA, and VTT Technical Research Centre of Finland, Espoo,
Finland, sixth edition, September 2013.
[2] K. McGrattan, S. Hostikka, R. McDermott, J. Floyd, C. Weinschenk, and K.
Overholt. Fire Dynamics Simulator, Technical Reference Guide, Volume 3:
Validation. National Institute of Standards and Technology, Gaithersburg,
Maryland, USA, and VTT Technical Research Centre of Finland, Espoo,
Finland, sixth edition, September 2013.
[3] Romet Limited, East Mississauga, Ontario. Rotary Gas Meter RM3000
Technical Specification, 2014.
[4] L.G. Blevins. Behavior of bare and aspirated thermocouples in compartment
fires. In National Heat Transfer Conference, 33rd Proceedings, pages 15–17,
1999.
[5] W.M. Pitts, E. Braun, R. Peacock, H. Mitler, E. Johnson, P. Reneke, and
L.G. Blevins. Temperature uncertainties for bare-bead and aspirated
thermocouple measurements in fire environments. ASTM Special Technical
Publication, 1427:3–15, 2003.

## Slide 90: References
[6] A. Lock, M. Bundy, E.L. Johnsson, A. Hamins, G.H. Ko, C. Hwang, P.
Fuss, and R. Harris. Experimental study of the effects of fuel type, fuel
distribution, and vent size on full-scale underventilated compartment fires
in an ISO 9705 room. NISTTN 1603, National Institute of Standards and
Technology, Gaithersburg, MD, 2008.
[7] R.A. Bryant. A comparison of gas velocity measurements in a full-scale
enclosure fire. Fire Safety Journal, 44:793–800, 2009.
[8] W.M. Pitts, A.V. Murthy, J.L. de Ris, J. Filtz, K. Nygard, D. Smith, and I.
Wetterlund. Round robin study of total heat flux gauge calibration at fire
laboratories. Fire Safety Journal, 41(6):459–475, 2006.
[9] B. McCaffery, J. Quintiere, and M. Harkleroad. Estimating Room Fire
Temperatures and the Likelihood of Flashover Using Fire Test Data
Correlations. Fire Technology, 17(2):98–119, 1981.
[10] K. McGrattan, S. Hostikka, R. McDermott, J. Floyd, C. Weinschenk, and
K. Overholt. Fire Dynamics Simulator, User’s Guide. National Institute of
Standards and Technology, Gaithersburg, Maryland, USA, and VTT
Technical Research Centre of Finland, Espoo, Finland, sixth edition,
September 2013.

## Slide 91: References
[11] K. Hill, J. Dreisbach, F. Joglar, B. Najafi, K. McGrattan, R. Peacock, and A.
Hamins. Verification and Validation of Selected Fire Models for Nuclear
Power Plant Applications. NUREG-1824, United States Nuclear Regulatory
Commission, Washington, DC, 2007.
[12] D. Gross. Data Sources for Parameters Used in Predictive Modeling of Fire
Growth and Smoke Spread. NBSIR 85-3223, National Bureau of
Standards (now NIST), Gaithersburg, Maryland, September 1988.
[13] USG Corporation, Chicago, IL. USG DUROCK Brand Cement Board
Submittal Sheet CB399, 2016.
[14] K. McGrattan and B. Toman. Quantifying the predictive uncertainty of
complex numerical models. Metrologia, 48:173–180, 2011.
[15] M.L. Janssens and H.C. Tran. Data Reduction of Room Tests for Zone
Model Validation. Journal of Fire Science, 10:528–555, 1992.